## Feuil1
SAFETY PLC INPUT/OUTPUT LIST
SAFETY INPUTS
PIN NAME | VARIABLE NAME | SHAPE/LEVEL | DESCRIPTION
I.0 | nh3_detector_open | A_pulse | NH3 gas detector, NC contact. Open when no gas is detected.
I.1 | nh3_detector_closed | A_pulse | NH3 gas detector, NO contact. Closed when no gas is detected.
I.2 | h2_detector1_closed | B_pulse | H2 gas detector central (GfG). Closed when no gas is detected.
I.3 | h2_detector2_closed | C_pulse | H2 gas detector 2 (Dega). Closed when no gas is detected.
I.4 | h2_detector2_open | Static | H2 gas detector 2 (Dega). Open when no gas is detected.
I.5 | h2_detector2_analog | Input, analogue | H2 gas detector 2 (Dega) analog input. 4..20mA to 1..5V through a 250 Ohm resistor. 1 count = 0.1V
I.6 | stop_button_container_NC | B_pulse | Stop button inside container. Closed when button is not pressed.
I.7 | stop_button_container_NO | B_pulse | Stop button inside container. Open when button is not pressed.
I.30 | supervision_relay_NC | B_pulse | "Supervision-Safety" interface relay. Closed when relay is de-energized.
I.31 | supervision_relay_NO | B_pulse | "Supervision-Safety" interface relay. Open when relay is de-energized.
I.32 | extractor1_command_NO | Static | Extractor 1 command. Open when user wants to turn it OFF. Closed when user wants to turn it ON.
I.33 | extractor1_pressure_NO | A_pulse | Extractor 1 pressure sensor. Closed when underpressure is detected (extractor ON). Open when no underpressure is detected (extractor OFF).
I.34 | extractors_available | C_pulse | Extractors 1 and 2 availability. Closed when both extractors are available. Open when thermal protections are triggered or 3-phase power is not available.
I.35 | reset_sound_alarm_NO | Static | Reset "safety action 1" (gas sound alarm). Closed when button is pressed. Note: the button is in series with several feedback NC contacts.
I.36 | reset_extractors_NO | Static | Reset "safety action 2" (extractors and visual alarm). Closed when button is pressed. Note: the button is in series with several feedback NC contacts.
I.37 | reset_shutdown_container_NO | Static | Reset "safety action 3" (container power shutdown). Closed when button is pressed. Note: the button is in series with several feedback NC contacts.
I.40 | stop_button_cabinet_NC | C_pulse | Stop button installed on CAB-2 door. Closed when button is not pressed.
I.41 | in_test_extractors_NO | Static | Test extractors 1 & 2. 0: No test. 1: Test activated.
I.42 | in_h2_detector1_fault_closed | A_pulse | H2 gas detector central (GfG). Closed when no default is detected.
NON-SAFETY OUTPUTS
PIN NAME | VARIABLE NAME | SHAPE/LEVEL | DESCRIPTION
IQ.10 | A_pulse_out | A_pulse | Dynamic output signal. Pulse train type A (marked as red-black cable in PL-005_rev04v01).
IQ.11 | B_pulse_out | B_pulse | Dynamic output signal. Pulse train type B (marked as blue-black cable in PL-005_rev04v01).
IQ.12 | C_pulse_out | C_pulse | Dynamic output signal. Pulse train type C (marked as magenta-black cable in PL-005_rev04v01).
IQ.13 | LED_system_online | Output, static | Indication light. Light ON: safety PLC is online. Light OFF: PLC is offline (power cut).
IQ.14 | LED_H2_alarm_non_latched | Output, static | Indication light. Light ON: at least one of the two H2 gas sensors is detecting a gas leak. Light OFF: none of the H2 gas sensors is detecting a gas leak.
IQ.15 | LED_H2_alarm_latched | Output, static | Indication light. Latched version of 'LED_H2_alarm_not_latched' signal.
IQ.16 | LED_NH3_alarm_non_latched | Output, static | Indication light. Light ON: NH3 gas sensor is detecting a gas leak. Light OFF: NH3 gas sensor is not detecting a gas leak.
IQ.17 | LED_NH3_alarm_latched | Output, static | Indication light. Latched version of 'LED_NH3_alarm_non_latched' signal.
IQ.20 | LED_extractors_out_of_service | Output, static | Indication light. Light ON: at least one extractor is out of service. Light OFF: both extractors are available.
IQ.21 | out_non_safety_gas_OK | Output, static | Indication. Activated: gas leak has been detected or safety system is out of service. Non activated: no gas has beed detected and safety system is online.
IQ.22 | out_non_safety_reset_sound_alarm | Output, static | Indication. Reset "safety action 2" (extractors and visual alarm) is ready to be reseted by pressing 'reset_sound_alarm_NO' button.
IQ.23 | out_non_safety_reset_extractors | Output, static | Indication. Reset "safety action 1" (gas sound alarm) is ready to be reseted by pressing 'reset_extractors_NO' button.
IQ.24 | out_non_safety_reset_shutdown | Output, static | Indication. Reset "safety action 3" (container power shutdown) is ready to be reseted by pressing 'reset_shutdown_container_NO' button.
IQ.25 | out_non_safety_fault_alarm | Output, static | 'OR' logic combination of all positive-logic fault variables.
SAFETY OUTPUTS
PIN NAME | VARIABLE NAME | DESCRIPTION
Q2 | out_safety_shutdown1 | Safety action 3. It commands: H2 electrovalve, electrolyzer, PV pannels.
Q3 | out_safety_shutdown2 | Safety action 3. It commands: container 3-phase power, fuel-cell Li-ion batteries.
Q4 | out_safety_sound_alarm | Safety action 1. It commands sound alarm.
Q5 | out_safety_extractors | Safety action 2. It commands extractors and visual alarm.